## Pu_actual calculator
Impedance PU-Actual Calculator
As of Three Phase
Input section(Base input)
kVbase | 33 |  | Freq? | 50 | hz |  | Input!
MVAbase | 100 | [5 empty] | Don't touch
Calculation of Zbase(ohm)
Zbase | 10.89 | ohm
Getting Actual Impedance |  |  |  | Getting Pu from actual value(Ohm)
Zbase | 10.89 |  |  | Zbase | 10.89 | ohm
Zpu? | 0.000394 |  |  | R(ohm)? | 2.3332 | ohm
Zactual(ohm) | 0.0042907 |  |  | R(pu) | 0.21425 | pu
Henry Converter
Zactual(ohm) | 0.0042907 | ohm |  | Getting pu from actual value(Henry)
Inductance | 1.3658e-05 | H |  | Zbase | 10.89 | ohm
| 0.013658 | mH |  | L?[H] | 0.0048274 | H
|  |  |  | converted Xl | 1.5166 | ohm
Farad Converter |  |  |  | XL(pu) | 0.13926 | pu
Zactual(ohm) | 0.0042907 | ohm
Conductance | 0.74187 | F |  | Getting pu from actual value(Farad)
| 741866.9533 | uF |  | Zbase | 10.89 | ohm
|  |  |  | C?[F] | 0.0020989 | [F]
|  |  |  | converted Xc | 1.5166 | ohm | 0.297 | 2.97e-07
|  |  |  | XC(pu) | 0.13926 | pu
Changing base
new base(MVA)? | 100
old base(MVA)? | 123.42
new (kV)? | 132
old (kV)? | 132
old pu? | 0.01088
new pu | 0.0088154

## Network pu impedanc calculation
From PVS980 ABB Formula
rules
Sk_net = $i1*$SCR
pi_cons = 3.141592653589793238462643 |  |  | Freq? | 50
Z_net = (($Un*1000)**2)/(Sk_net*1.0e6)
R_net = Z_net*cos(atan($X_R_net))
L_net = (Z_net*sin(atan($X_R_net)))/(2*pi_cons*$i2)
Sk_net | 312.18
Input section |  |  |  | Applying MVA | 100
Nominal Hz | 50 |  |  | Applying Vnom | 132
PlantMVA | 156.09 |  |  |  | 174.24
SCR | 2
Vnom | 132
X/R ratio | 10
Calcaulted Section
Z_net | 55.814 | ohm | Zbase | 174.24 | ohm
R_net | 5.5537 | ohm | Ractual | 5.5537 | ohm
L_net[H] | 0.17678 | H | Xl_actual | 55.537 | ohm
L_net[ohm] | 55.537 | ohm
|  |  | Rpu | 0.031874 | pu
|  |  | Xpu | 0.31874 | pu
|  |  | X/R | 10

## Droop Formula by AEMO
AEMO Droop Standard
% Droop
FB | 1 | frequency deviation at which the maximum charge or discharge of the BESS
D | 0.15 | frequency dead band which has a default value, 0.15
C | 50 | registered capacity of the BESS
SP | 50 | capacity of the BESS used to provide an FCAS response.
%Droop | 1.7 | % | Droop pu | 0.017
Contingency FCAS Capacity(Or manually FCAS capacity can be derived from chaing %Droop below)
%droop | 1.7 | %
FB | 1 | frequency deviation at which the maximum charge or discharge of the BESS
FR | 1 | absolute value of the difference between 50 Hz and the raise or lower reference frequency
D | 0.15 | frequency dead band which has a default value, 0.15
C | 50 | registered capacity of the BESS
Contringency FACS Capacity |  |  | 50

## Droop and FCAS capacity cal
FCAS capacity Cal
%Droop | 1.7
FR | 1
Hz | MW
49 | 50
49.05 | 47.0588
49.1 | 44.1176
49.15 | 41.1765
49.2 | 38.2353
49.25 | 35.2941
49.3 | 32.3529
49.35 | 29.4118
49.4 | 26.4706
49.45 | 23.5294
49.5 | 20.5882
49.55 | 17.6471
49.6 | 14.7059
49.65 | 11.7647
49.7 | 8.8235
49.75 | 5.8824
49.8 | 2.9412
49.85 | 0
49.9 | 0
49.95 | 0
50 | 0
50.05 | 0
50.1 | 0
50.15 | 0
50.2 | -2.9412
50.25 | -5.8824
50.3 | -8.8235
50.35 | -11.7647
50.4 | -14.7059
50.45 | -17.6471
50.5 | -20.5882
50.55 | -23.5294
50.6 | -26.4706
50.65 | -29.4118
50.7 | -32.3529
50.75 | -35.2941
50.8 | -38.2353
50.85 | -41.1765
50.9 | -44.1176
50.95 | -47.0588
51 | -50